BigWatt Digital Upsized Gas-Powered Data Center Sites
Air Permit Submissions, Decarbonization Deliverables, and Brick Full-Service Execution Plan

Prepared as a presentation-ready permitting workplan positioning Brick as the full air-water-permitting + energy supply/optimization + decarbonization execution partner, including workstreams that may otherwise be led by ASG or similar consultants.

# Executive Positioning

BigWatt's upsized sites face an air-permitting problem driven by Potential to Emit (PTE), modeled ambient impacts, enforceable operating limits, public scrutiny, and the ability to show that onsite generation can operate within a defensible emissions envelope. Brick should not be positioned only as a software efficiency add-on. Brick should be positioned as the single technical owner for the air-water-permit submission package and the post-issuance compliance operating system.

Brick's expanded role: prepare or directly manage all air-permit deliverables; generate the PTE, BACT/LAER, dispersion modeling, monitoring, recordkeeping, and decarbonization packages; translate permit limits into live operational controls; and provide the software layer that proves compliance after COD.

# Critical Regulatory Correction

Subpart KKKK applies to new, modified, or reconstructed stationary combustion turbines under 40 CFR Part 60. For modern gas turbines at BigWatt sites, this is the core NSPS rule set.

Subpart YYYY is not the primary backup-engine rule. In this context, Subpart YYYY is a 40 CFR Part 63 NESHAP for stationary combustion turbines at major HAP sources. Backup reciprocating engines are typically evaluated under 40 CFR Part 60 Subpart IIII for compression-ignition engines, Subpart JJJJ for spark-ignition engines, and 40 CFR Part 63 Subpart ZZZZ for RICE NESHAP applicability.

# Air Permit Package BigWatt Must Deliver

| Submission / Report | What permitting body needs | Brick deliverable BigWatt can present | Priority |
| --- | --- | --- | --- |
| 1. Air Construction Permit Application Forms | State/local construction permit forms with facility identity, source description, requested permit action, source classification, controls, emissions units, and compliance certifications. | Brick Permit Application Binder: completed application forms, facility narrative, emissions-unit schedule, requested synthetic minor/major permit strategy if applicable, and permit-condition request language. | Immediate |
| 2. Project Description + Site Development Narrative | Clear description of upsized data center campus, onsite generation concept, fuel supply, turbines, emergency/black-start assets, cooling systems, battery/thermal assets, and operating philosophy. | Brick Site + Source Narrative: permitting-grade text, process flow diagrams, equipment hierarchy, emissions-unit IDs, stack IDs, operating scenarios, and site expansion logic. | Immediate |
| 3. Equipment Schedule / Source List | Every emissions source must be listed: turbines, HRSG if any, duct burners, emergency engines, fire pumps, boilers, fuel heaters, tanks, fugitive sources, and construction equipment if required. | Brick Emissions Unit Register: controlled source inventory with manufacturer, model, rating, heat input, fuel, stack parameters, control device, monitoring points, and permit limit linkage. | Immediate |
| 4. Regulatory Applicability Determination | Determination of PSD/NSR/NNSR, Title V, NSPS KKKK/KKKKa if relevant, NESHAP YYYY, RICE IIII/JJJJ/ZZZZ, state toxics, GHG, and local rules. | Brick Applicability Memo: rule-by-rule applicability matrix and decision tree. Includes threshold calculations and source classification logic for the upsized site. | Immediate |
| 5. Potential to Emit (PTE) Analysis | Maximum emissions capability before enforceable limits. PTE determines whether site is major, PSD/NNSR applicability, Title V, HAP major status, and modeling burden. | Brick PTE Workbook: uncontrolled, controlled, and proposed enforceable PTE by pollutant and emissions unit; scenario-based hourly, daily, monthly, annual calculations. | Immediate |
| 6. Controlled Emissions Inventory | Annual and short-term emissions estimates for NOx, CO, VOC, PM/PM10/PM2.5, SO2, CO2e, HAPs, formaldehyde, and startup/shutdown events. | Brick Controlled Emissions Workbook: OEM curves + EPA factors + fuel specs + load profiles + control efficiencies + startup/shutdown factors. | Immediate |
| 7. Operating Scenario Matrix | Permitting body needs to understand normal operation, peak ambient operation, startup/shutdown, commissioning, emergency operation, maintenance, and upset/malfunction assumptions. | Brick Operating Scenario Matrix: mode-by-mode dispatch profile with runtime hours, loads, turbine starts, battery use, thermal shifting, and emissions impact. | Immediate |
| 8. BACT Analysis for PSD | If PSD major, applicant must show top-down Best Available Control Technology for each regulated pollutant and affected source. | Brick BACT Report: SCR/oxidation catalyst/dry-low-NOx/combustion controls, vendor guarantees, feasibility, cost-effectiveness, collateral impacts, proposed limits. | High |
| 9. LAER + Offsets if Nonattainment NSR | If located in nonattainment area and thresholds are exceeded, Lowest Achievable Emission Rate and emission reduction credits may be required. | Brick LAER/Offset Strategy: LAER alternatives, offset requirement estimate, ERC strategy, and operating-limit alternatives to avoid NNSR where possible. | High / site-specific |
| 10. Air Dispersion Modeling Protocol | Regulator often requires modeling plan before final modeling: sources, stack parameters, terrain, met data, receptors, building downwash, pollutants, averaging periods. | Brick Modeling Protocol: AERMOD-ready source inventory, receptor grid, stack data, BPIP/downwash inputs, meteorological data selection, background concentration plan. | High |
| 11. Air Dispersion Modeling Report | Demonstrate modeled concentrations do not cause or contribute to NAAQS/PSD increment exceedances or unacceptable toxic impacts. | Brick AERMOD Report Package: model files, inputs, results tables, exceedance analyses, maps, sensitive receptor analysis, and mitigation options. | High |
| 12. Preconstruction Ambient Air / Background Analysis | Permitting body may require background concentration data, monitoring justification, or preconstruction monitoring waiver analysis. | Brick Ambient Data Memo: monitor selection, representativeness, background values, temporal pairing, and waiver/monitoring strategy. | High |
| 13. Additional Impact Analysis | PSD applications can require additional impacts: growth, soils, vegetation, visibility, Class I area screening if relevant. | Brick Additional Impacts Report: growth/employment/load impacts, vegetation/soil screening, visibility/Class I applicability, community sensitivity map. | Medium / PSD |
| 14. GHG / Decarbonization Analysis | Even when GHG alone does not trigger PSD, GHG analysis, energy efficiency, and carbon strategy are increasingly important for approval and stakeholder defense. | Brick Decarbonization + GHG Report: CO2e inventory, heat-rate optimization, cooling-load reduction, battery/thermal dispatch, renewable/RNG/hydrogen optionality, avoided emissions. | High |
| 15. Monitoring, Testing, and Compliance Plan | Regulators require enforceable monitoring: CEMS/PEMS/CPMS, stack tests, fuel monitoring, turbine operating parameters, SCR ammonia slip if applicable. | Brick Monitoring Plan: CEMS/PEMS architecture, data acquisition, sensor list, emissions proxy, data validation, QA/QC, stack test schedule, dashboard/reporting format. | High |
| 16. Recordkeeping and Reporting Plan | Permit must define records retained and periodic reports submitted: runtime, fuel, emissions, deviations, maintenance, startups, shutdowns, tests. | Brick Compliance Data Room: automated logs, permit-limit tracker, deviation workflow, monthly/quarterly/semiannual reports, Title V-ready certification package. | High |
| 17. Public Notice / Hearing Support Package | Large gas-powered data centers may face public scrutiny. Technical defensibility and decarb story matter. | Brick Public Support Binder: plain-English emissions explanation, decarb plan, avoided emissions, water/energy narrative, Q&A, response-to-comments technical appendix. | Medium / High |
| 18. Draft Permit Condition Matrix | Applicant should propose practical limits and conditions to avoid unworkable permit language. | Brick Permit Condition Matrix: proposed limits, measurement method, data source, responsible system, compliance demonstration, and operational feasibility check. | Immediate |
| 19. Post-Issuance Compliance Implementation | After permit grant, the facility must operate within conditions and produce records during inspections. | Brick Compliance OS: operational controls that enforce runtime, dispatch, emission-rate, fuel, startup/shutdown, and reporting constraints. | Post-permit but design now |

# How Brick Covers the ASG-Style Scope End-to-End

For BigWatt, Brick can own the full package while still collaborating with ASG if BigWatt wants ASG involved. The messaging should be: Brick is not dependent on ASG to define the permit case; Brick can produce the technical artifacts, manage the consultant workflow, interface with permitting counsel, and convert approved permit limits into operational software controls.

| ASG-type workstream | Brick full-service coverage |
| --- | --- |
| Site development / pad-ready strategy | Brick creates the air-permit-ready basis of design, siting constraints register, stack/source locations, load and generation assumptions, and VDR-ready permit artifacts. |
| Permitting strategy | Brick prepares PSD/NNSR/Title V/synthetic-minor strategy, rule applicability memo, PTE scenarios, and pre-application meeting materials. |
| Technical filings | Brick produces application forms, emissions calculations, BACT/LAER analyses, modeling protocol, AERMOD package, GHG/decarb report, monitoring plan, and public-comment package. |
| Transaction readiness / VDR | Brick creates lender/buyer diligence folders: permit status tracker, regulatory risk register, emissions model, permit condition matrix, capex/opex impacts, decarb roadmap. |
| Post-permit compliance | Brick implements runtime, fuel, startup/shutdown, turbine dispatch, battery dispatch, and cooling optimization controls that generate compliance records automatically. |

# Brick Decarbonization Levers Tied Directly to Permit Submissions

| Permit objective | Brick technical method | Resulting submission |
| --- | --- | --- |
| Reduce PTE or proposed enforceable PTE | Use smaller guaranteed load envelope, lower cooling load, enforceable annual runtime caps, and dispatch constraints. | PTE workbook; operating limit proposal; permit condition matrix |
| Reduce NOx and CO modeled emissions | Optimize turbine load bands, reduce starts, implement SCR/oxidation catalyst assumptions, reduce auxiliary cooling load. | BACT report; controlled emissions workbook; startup/shutdown memo |
| Improve AERMOD outcomes | Lower hourly emission rates, optimize stack parameters, source locations, building downwash assumptions, and load scenarios. | Modeling protocol; AERMOD report; mitigation memo |
| Reduce public opposition | Quantify avoided fuel burn, avoided CO2e, lower PUE, lower water/energy waste, and transparent compliance monitoring. | Public support binder; GHG/decarbonization report |
| Make permit limits enforceable | Translate permit constraints into live controls, alarms, automated logs, and reports. | Monitoring plan; Compliance OS; Title V-ready reporting package |

# Immediate 30-Day Workplan for BigWatt

| Timing | Workstream | Concrete output |
| --- | --- | --- |
| Days 1-3 | Kickoff + data request | Collect turbine models, site layout, MW capacity, fuel specs, cooling design, battery/thermal assets, operating assumptions, ambient data, stack info, and upsizing scope. |
| Days 4-7 | Regulatory + PTE screen | Determine PSD/NNSR/Title V/HAP major triggers; identify whether synthetic-minor / enforceable limits can avoid major review. |
| Days 8-14 | Emissions model + permit strategy | Build PTE/controlled emissions workbook; draft operating scenario matrix; define minimum decarbonization and controls needed to reduce permit risk. |
| Days 15-21 | BACT/LAER + modeling protocol | Prepare top-down control technology analysis; prepare AERMOD protocol and source/receptor setup; identify mitigations before formal filing. |
| Days 22-30 | Pre-application package | Deliver pre-application meeting deck, permit application skeleton, source list, PTE workbook, draft permit limits, compliance plan, and regulator Q&A. |

# Data Request BigWatt Should Send Brick Immediately

Turbine make/model, quantity, MW rating, heat input, heat rate curve, fuel type, guaranteed NOx/CO/VOC/PM/SO2/CO2e/HAP emission rates, startup/shutdown data, and control device specs.

Backup/black-start engine make/model, horsepower/kW, emergency vs non-emergency use, fuel, operating hours, stack data, and applicable certifications.

Site plan, plot plan, building dimensions, stack locations, stack heights/diameters, exhaust temperature/velocity, property boundary, nearby receptors, and terrain constraints.

Data center load profile: IT MW by phase, cooling design, PUE target, chiller/CDU/CRAH/CRAC equipment, pumps/fans/towers, thermal storage, battery systems, and operating modes.

Upsizing delta: original permitted or contemplated MW vs upsized MW; construction phasing; desired COD; targeted state/county/local jurisdiction.

Prior correspondence with permitting body, ASG work product, utility/gas constraints, public opposition risk, environmental justice screening, and local air-quality status if available.

# Recommendations

Brick can cover the full air-permit technical package and the decarbonization operating plan for BigWatt upsized sites. We can prepare the emissions inventory, PTE analysis, BACT/LAER strategy, dispersion modeling package, compliance monitoring plan, public-response materials, and permit-condition matrix, then operationalize the permit through software controls that reduce turbine runtime, cooling load, fuel burn, startup/shutdown events, and emissions intensity.

# Sources / Regulatory References

EPA NSR/PSD program overview: https://www.epa.gov/nsr

40 CFR Part 60 Subpart KKKK - stationary combustion turbines: https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-60/subpart-KKKK

40 CFR Part 63 Subpart YYYY - stationary combustion turbines NESHAP: https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-63/subpart-YYYY

40 CFR Part 60 Subpart IIII - stationary compression ignition engines: https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-60/subpart-IIII

40 CFR Part 60 Subpart JJJJ - stationary spark ignition engines: https://www.ecfr.gov/current/title-40/chapter-I/subchapter-C/part-60/subpart-JJJJ

EPA AERMOD / preferred dispersion models: https://www.epa.gov/scram/air-quality-dispersion-modeling-preferred-and-recommended-models

ASG site development services: https://asg-team.com/